## Combustion Turbines
NO2 - NOx Instack Ratios Per Source Tests Approved by the Alaska Department of Environmental Conservation
Average Results for Given Load/Condition for Combustion Turbines
Last Update: | 2013-08-23
Stationary Source | Mfg | Model | NOx Control | Other Post-Combustion Control | Size | Size units | Fuel Type | Test Date | Intake Temp (F) | Percent Load | NOx (ppmv) | NO2 (ppmv) | NO2 / NOx | Comments
BP Caribou Crossing | Solar | Centaur | SoLoNOx | None | 5978 | hp | Gas | 2003-06-01 | 41 | 100 | 21.1 | 2.3 | 0.109
[9 empty] | 41 | 80 | 11.2 | 3.7 | 0.33036
[9 empty] | 40 | 40 | 10.9 | 3.8 | 0.34862
[9 empty] | 43 | 20 | 16.3 | 14.4 | 0.88344
BP CCP | GE | MS5382C | Diffusion | None | 38000 | hp | Gas | 2006-02-17 | 14.5 | 100 | 78.85 | 6.8 | 0.08624
[9 empty] | 15.7 | 80 | 57 | 5.7 | 0.1
[9 empty] | 13.8 | 60 | 46.5 | 6.2 | 0.13333
| GE | MS5371PATP | LHE | None | 35800 | hp | Gas | 2006-02-15 | 27.2 | 80 | 49.6 | 14.65 | 0.29536
[9 empty] | 27.8 | 60 | 40 | 21.4 | 0.535
| GE | MS5371PATP | Diffusion | None | 35400 | hp | Gas | 2006-02-16 | 29.7 | 80 | 81.7 | 7.2 | 0.088127
[9 empty] | 31.8 | 60 | 71.45 | 6.15 | 0.086074
BP CGF | GE | MS6491 | Diffusion | None | 53665 | hp | Gas | 2005-07-16 | 36.3 | 100 | 103.6 | 9.7 | 0.093629
[9 empty] | 37 | 80 | 104.6 | 9.7 | 0.092734
| Rolls Royce | RB211-24C | Diffusion | None | 33300 | hp | Gas | 2006-06-23 | 38 | 100 | 101.6 | 2.2 | 0.021654
[9 empty] | 48 | 80 | 89.6 | 10.9 | 0.12165
[9 empty] | 46 | 60 | 78.9 | 13.8 | 0.1749
BP CPS | GE | MS5001R | Diffusion | None | 20500 | kWe | Gas | 2004-12-10 | -22 | 100 | 65.7 | 4.7 | 0.071537
[9 empty] | -24.3 | 80 | 51.7 | 5.6 | 0.10832
[9 empty] | -25.3 | 60 | 40.2 | 6 | 0.14925
[9 empty] | -27.7 | 40 | 30.6 | 5.9 | 0.19281
BP Endicott | Ruston | Tornado | Diffusion | None | 8717 | hp | Gas | 2006-06-11 | 45 | 80 | 45.4 | 2.2 | 0.048458
[9 empty] | 45 | 60 | 34.9 | 3.8 | 0.10888
[9 empty] | 45 | 20 | 21.4 | 6.9 | 0.32243
BP FS#3 | GE | MS5322R | Diffusion | None | 32000 | hp | Gas | 2005-07-11 | 46.2 | 100 | 108.1 | 3.35 | 0.03099
[9 empty] | 46.3 | 80 | 91.45 | 4.6 | 0.050301
BP GC#2 | Sulzer | S3 | DiffusionDies | None | 7970 | hp | Gas | 2006-06-26 | 48 | 60 | 87.7 | 9.8667 | 0.1125
[9 empty] | 47.3 | 40 | 62 | 16.8 | 0.27097
BP GC#3 | GE | MS5352B | LHE | None | 35000 | hp | Gas | 2005-07-29 | 39.7 | 100 | 47.1 | 14.5 | 0.30786
[9 empty] | 41 | 80 | 42.9 | 14.5 | 0.338
BP LPC | Solar | Mars | Diffusion | None | 8950 | kWe | Gas | 2004-12-07 | -14 | 80 | 87.9 | 9.87 | 0.11229
[9 empty] | -9 | 60 | 54.6 | 8.5 | 0.15568
[9 empty] | -8.4 | 40 | 37.7 | 13.8 | 0.36605
BP Milne Point | GE | LM2500 | Diffusion with H2O Injection | None | 29500 | hp | Diesel | 2009-08-07 | 42 | 80 | 155.6 | 12.8 | 0.08
[9 empty] | 46.2 | 60 | 101.3 | 9.2 | 0.090819
[9 empty] | 43.5 | 40 | 52.5 | 14.7 | 0.28
[7 empty] | Gas |  | 41 | 80 | 113.6 | 11.7 | 0.1
[9 empty] | 42 | 60 | 79.5 | 11.6 | 0.14591
[9 empty] | 50 | 40 | 47.3 | 10.1 | 0.21
BP Northstar | Solar | Mars | SoLoNOx | None | 9100 | kWe | Gas | 2003-09-10 | 35 | 60 | 21.6 | 4.3 | 0.19907
[9 empty] | 36.3 | 40 | 26.9 | 6.5 | 0.24164
[9 empty] | 39.7 | 20 | 21 | 6.6 | 0.31429
| GE | LM2500 | DLE | None | 30500 | hp | Gas | 2003-02-27 | 0 | 100 | 17.925 | 2.85 | 0.159
XTO Energy Platform A | Solar | Saturn T-1301 | None | None | 1300 | hp | Gas | 2012-02-12 | 22 | 60 | 31 | 4.8 | 0.15484
[8 empty] | 2013-04-13 | 34 | 60 | 45 | 5.4 | 0.12
Alyeska Pump Station # 3 | Siemens | SGT 400 | Dry Low Emissions Technology | None | 12900 | kW | Gas | 2012-07-26 | 70 | 100 | 10 | 0.7 | 0.07
[9 empty] | 71 | 80 | 23 | 2.8 | 0.12174
[9 empty] | 70 | 60 | 17 | 5.5 | 0.32353
[9 empty] | 70 | 40 | 13 | 2.6 | 0.2
North Pole Power Plant | GE | Frame 7, Series 7001 | None | None | 627 | MMBtu/hr | Fuel Oil | 2012-02-28 | Not Available | 50 | 169 | 0.6 | 0.0035503
|  | LM6000PC | Water Injection | Catalytic Oxidation | 455 | MMBtu/hr | Naphtha | 2013-03-01 | Not Available | 50 | 95 | 38.2 | 0.40211

## Reciprocating Engines
NO2 - NOx Instack Ratios Per Source Tests Approved by the Alaska Department of Environmental Conservation
Average Results for Given Load/Condition for Recipricating Engines
Last Update: | 2013-08-23
Stationary Source | Mfg | Model | NOx Control | Other Post-Combustion Control | Size | Size Units | Fuel Type | Test Date | Intake Temp (F) | Percent Load | NOx (ppmv) | NO2 (ppmv) | NO2 / NOx | Comments
BP Northstar | Cummins | QSK60-G6 | None | None | 2660 | kWe | Diesel | 2004-07-08 | 51 | 80 | 1149.8 | 53 | 0.046095 | Emergency generator
[9 empty] | 51 | 60 | 960.5 | 38.8 | 0.040396
[9 empty] | 51 | 40 | 846.1 | 33.5 | 0.039593
Trident Akutan | Caterpilar | 3516B | Low Nox | None | 1655 | kWe | Diesel | 2005-12-01 | 152 | 100 | 1329.62 | 127.86 | 0.096163 | Quad Turbo Electric Generator, Pollock Gen 1, Air intake near turbo unit
[9 empty] | 133 | 80 | 1347.26 | 120.92 | 0.089753
[9 empty] | 105 | 60 | 1087.6 | 99.52 | 0.091504
| Caterpilar | 3512B | Low Nox | None | 1360 | kWe |  |  | 128 | 100 | 1247 | 83.55 | 0.067001 | Quad Turbo Electric Generator, Pollock Gen 2, Air intake near turbo unit
[9 empty] | 138 | 80 | 1267.97 | 95.78 | 0.075538
[9 empty] | 101 | 60 | 982 | 110.33 | 0.11235
| Caterpilar | 3508B |  | None | 2.69 | MMBtu/hr |  |  | 150 | 80 | 523.41 | 26.61 | 0.05084 | Twin Turbo Compressor
AEL&P Lemon Creek | EMD | 20-6450E4 | None | None | 2600 | kWe | Diesel | 2008-08-21 |  | 100 | 960 | 43 | 0.04 | 1966 2-stroke engine
[10 empty] | 80 | 824 | 20.7 | 0.03
CPAI Beluga River | Waukesha | F3514GSI | 3-way cat | None | 740 | hp | NG | 2012-01-20 | 15 | 80 | 54 | 2.6333 | 0.048765
| Waukesha | FG18GSI | 3-way cat | None | 400 | hp |  | 2012-01-23 | 24 | 80 | 71 | 20.3 | 0.28592
| Waukesha | F3514GSI | 3-way cat | None | 740 | hp |  | 2012-02-15 | 35 | 100 | 51 | 2.6 | 0.05098
[9 empty] | 34 | 80 | 74 | 1.03 | 0.013919
[9 empty] | -2 | 60 | 49 | 3 | 0.061224
| Waukesha | FG18GSI | 3-way cat | None | 400 | hp |  | 2012-01-25 | 7 | 80 | 55.7 | 6.7 | 0.12029
Tok Power Generation Station | Caterpilar | 3516B | None | None | 1285 | kW | Diesel | 2012-04-11 | 72 | 80 | 1128 | 76.2 | 0.067553
[9 empty] | 80 | 60 | 1183 | 78.7 | 0.066526
[9 empty] | 71 | 40 | 901 | 54.7 | 0.06071
| Caterpilar | 3516 | None | None | 1135 | kW |  | 2012-04-15 | 74 | 100 | 1963 | 123.4 | 0.062863
[9 empty] | 75 | 60 | 1986 | 148.2 | 0.074622
[9 empty] | 76 | 40 | 1534 | 128.4 | 0.083703
| Caterpilar | C175-16 | None | None | 1930 | kW |  | 2012-04-12 | 81 | 60 | 503 | 14.5 | 0.028827
[9 empty] | 76 | 40 | 499 | 14.4 | 0.028858
[9 empty] | 71 | 20 | 515 | 18.2 | 0.03534
| Caterpilar | 3516 | None | None | 440 | kW |  | 2012-04-16 | 76 | 100 | 2241 | 167 | 0.07452
[9 empty] | 75 | 60 | 1914 | 133.3 | 0.069645
[9 empty] | 75 | 20 | 1186 | 79.9 | 0.067369
| Caterpilar | 3512C | None | None | 1050 | kW |  | 2012-04-14 | 76 | 100 | 726 | 19.4 | 0.026722
[9 empty] | 76 | 60 | 559 | 12.3 | 0.022004
[9 empty] | 74 | 40 | 415 | 15 | 0.036145
Dutch Harbor Power Plant | Wartsila | 12V32C | None | None | 5211 | kWe | Diesel | 2011-02-02 | Not Available | 60 | 1125 | 62.1 | 0.0552
| Caterpilar | C-280 | Centriugal Collector | None | 4400 | kWe | Diesel | 2012-08-08 | 67 | 100 | 1066 | 48 | 0.045028
Dillingham Power Plant | Caterpilar | 3512B | None | None | 1050 | kWe | Diesel | 2012-10-04 | 151 | 100 | 1029.5 | 63.1 | 0.061292
[9 empty] | 73 | 80 | 834 | 37.7 | 0.045204
[9 empty] | 72 | 60 | 666 | 22.5 | 0.033784
[9 empty] | 67 | 20 | 571 | 28.1 | 0.049212
Peter Pan Seafoods King Cove Facility | Caterpilar | 3412 | None | None | 1.54 | MMBtu/hr | Diesel | 2012-10-28 | Not Available | 100 | 657 | 34.8 | 0.052968
| Caterpilar | 3606 | None | None | 1500 | kW |  | 2012-10-23 |  | 100 | 1861 | 147 | 0.07899
[10 empty] | 80 | 1869 | 146.8 | 0.078545
[10 empty] | 60 | 1799 | 141.1 | 0.078432
[10 empty] | 40 | 1674 | 129.8 | 0.077539
| Caterpilar | 3516 | None | None | 1100 | kW |  | 2012-10-25 |  | 100 | 1833 | 138.1 | 0.075341
[10 empty] | 80 | 1882 | 154.7 | 0.0822
[10 empty] | 60 | 1860 | 165.2 | 0.088817
[10 empty] | 40 | 1665 | 164.2 | 0.098619
| Caterpilar | 3512 | None | None | 810 | kW |  | 2012-10-27 |  | 100 | 1842 | 146.5 | 0.079533
[10 empty] | 80 | 1875 | 155 | 0.082667
[10 empty] | 60 | 1857 | 163.9 | 0.088261
[10 empty] | 40 | 1789 | 171.5 | 0.095864
| Detroit Diesel | 16V149TI | None | None | 1000 | kW |  | 2012-10-26 |  | 60 | 796 | 32.5 | 0.040829
[10 empty] | 40 | 533 | 26.45 | 0.049625
DU-JBER-Electric, Gas, Drinking Water and Sanitary Services | Jenbacher | JGS 420 | GE LEANOX System | None | 1966 | bhp | Diesel | 2012-11-26 | 45 | 100 | 95 | 21 | 0.22105

## Heaters - Boilers
NO2 - NOx Instack Ratios Per Source Tests Approved by the Alaska Department of Environmental Conservation
Average Results for Given Load/Condition for Heaters and Boilers
Last Update: | 2013-08-23
Stationary Source | Mfg | Model | NOx Control | Other Post-Combustion Control | Size | Size units | Fuel Type | Test Date | Intake Temp (F) | Percent Load | NOx (ppmv) | NO2 (ppmv) | NO2/NOx | Comments
BP MPU | Zeeco | GLSFWB12 | Lo-NOx | None | 30 | MMBtu/hr, LHV | Gas | 2004-10-08 | 22 | 60 | 27.6 | 1.5 | 0.05
[9 empty] | 26 | 40 | 29.8 | 10.2 | 0.34
Healy Power Plant | Foster-Wheeler |  | Baghouse | None | 327 | MMBtu/hr | Coal | 2012-03-28 | 87 | 100 | 55.7 | 0.3 | 0.005386
[8 empty] | 2013-02-26 | Not Available | 100 | 163 | 2.5 | 0.015337
Dutch Harbor Seafood Processing Facility - Captain's Bay Plant | Cleaver- Brooks Fire Tube Boiler |  | None | None | 29.3 | MMBtu/hr | 70:30 Mix Fish Oil to Diesel | 2011-07-01 | 71 | 100 | 95 | 1 | 0.010526
[9 empty] | 72 | 80 | 89.5 | 1.2 | 0.013408
[9 empty] | 69.5 | 60 | 118.5 | 0.7 | 0.0059072
[9 empty] | 68 | 20 | 99 | 0.15 | 0.0015152
[7 empty] | Diesel | 2011-07-02 | 74 | 100 | 68 | 0.5 | 0.0073529
[9 empty] | 74 | 80 | 64 | 0.4 | 0.00625
[9 empty] | 69 | 60 | 76 | 0.4 | 0.0052632
[9 empty] | 71 | 20 | 79 | 0.1 | 0.0012658

## Incinerators
NO2 - NOx Instack Ratios Per Source Tests Approved by the Alaska Department of Environmental Conservation
Average Results for Given Load/Condition for Incinerators
Last Update: | 2013-08-23
Stationary Source | Mfg | Model | NOx Control | Other Post-Combustion Control | Rating | Rating units | Fuel Type | Test Date | Intake Temp (F) | Percent Load | NOx (ppmv) | NO2 (ppmv) | NO2/NOx | Comments
John M. Asplund Water Pollution Control Facility | Zimpro |  | Venturi Scrubber | Impingement Type Wet Scrubber | 2280 | lbs of dry sludge per hour | Biomass Solids | 2012-09-05 | 60 | 100 | 126 | 65.1 | 0.51667
¦