## January 2021 ETT
January 2021 ETT List
Note: Column titled "Est. New ETT Score" is the estimated new score based on the violations that have Returned to Compliance (RTCd) during the Quarter. Please note that this score will likely change on the next quarter's list due to further violations being generated. Comments submitted by Drinking Water Program staff on February 17, 2021.
Program Staff | RMW | Est. New ETT Score | System Information | 10 Point |  | 5 Point | [7 empty] | 1 Point | [12 empty] | General ETT Comments | How to Return to Compliance | Known Hardware Problems
|  |  |  | RTCR | SW | RTCR | SW | GWR | Nitrate | Arsenic | DBPs | LCR | Rads | RTCR | TCR | SW | GWR | Arsenic | DBPs | LCR | IOC | VOC | SOC | Rads | CCR | PN
VANSANDT | DEC | 20 | AKHIOK / AK2250037 (90 / C) | [5 empty] | 1 | [6 empty] | 4 |  | 1 | 5 |  | 1 | 1 |  |  |  |  | Last sampled for annual Nitrate in 2018, Arsenic in 2009, DBP2 (TTHM & HAA5) in 2018, IOCs in 2010, VOCs in 2018, and no distribution chlorine residual collected from 7/2019-2020. Fails to consistently submit MORs (last MOR in 9/2020). | Monitor for annual Nitrate, monthly TC with distribution chlorine residual, Arsenic, IOCs, VOCs, and DBP2. Consistently submit monthly MORs with adequate chlorine and turbidity data. | N/A
VANSANDT | DEC | 32 | AKUTAN / AK2260252 (95 / C) | [12 empty] | 27 |  |  | 1 | 1 | [6 empty] | Fails to comply with LT2 monitoring reportedly due to lack of sufficient funding. | In 2021, sample for E.coli (LT2), Lead/Copper, and TTHM & HAA5 (DBP2). | N/A
STATZ | YKHC | 99 | ALAKANUK WATER SYSTEM / AK2270362 (570 / C) | [5 empty] | 4 | [6 empty] | 30 |  |  | 37 | 2 | 1 | 4 |  |  |  |  | Last sampled for annual Nitrate in 03/2015, monthly TOC in 01/2016, LT2 in 08/2017, TTHM and HAA5 in 10/2015, Lead/Copper in 09/2012, IOCs in 05/2010, and VOC sin 03/2015. Also, last adequate amount of EP chlorine data reported in 05/2019. | Begin monitoring for the following contaminants: Nitrate, E. coli (LT2), TTHM, HAA5, TOC, Lead/Copper, IOCs, and VOCs. Also, submit a complete MOR with an adequate amount of EP chlorine data. | N/A
VANSANDT | No RMW | 11 | ALASKA RAINBOW LODGE / AK2261680 (36 / NC) | [5 empty] | 1 |  |  |  |  | 5 | [12 empty] | Last sampled for Nitrate in 2018 and last TC result submitted in 8/2019. | If operating in 2021, sample for Nitrate and TC. | N/A
MORRISON | No RMW | 12 | ALASKA WEST KANEKTOK RIVER CAMP / AK2272003 (44 / NC) | [5 empty] | 2 | [17 empty] | Last sampled for Nitrate in 2017. System did not operate in 2020 due to COVID-19. | Sample for Nitrate in 2021. | N/A
MORRISON | YKHC | 27 | ANVIK WATER SYSTEM / AK2280171 (96 / C) | [5 empty] | 2 | [7 empty] | 1 |  | 5 | 6 | 1 | [5 empty] | Last sampled for Nitrate in 2017, DBPs in 2010, Lead/Copper in 2016 and IOCs in 2010. Failed to collect a triggered source sample after TC+ result in 2018. | Sample for Nitrate, Lead/Copper, IOCs and collect a triggered source sample in 2021. Sample DBPs in 07/2021. | N/A
MORRISON | YKHC | 12 | ATMAUTLUAK WATER SYSTEM / AK2271033 (311 / C) |  |  |  |  | 2 | [18 empty] | Overdue sanitary survey deficiencies from 2017 inspection. | Address sanitary survey deficiencies. | N/A
LATIMER | No RMW | 12 | BAY VIEW TRAILER COURT / AK2241101 (51 / C) | [10 empty] | 8 | [10 empty] | 3 |  | Last sampled for TC in 2019. No CCR submitted for 2019 and 2020. | Sample for TC and provide 2019 and 2020 CCRs. | N/A
GILLESPIE | No RMW | 11 | BEAR CREEK RV PARK / AK2240773 (62 / NC) | [5 empty] | 1 | [7 empty] | 1 | [9 empty] | System did not operate in 2020 due to COVID-19. | Sample for Nitrate. Sample for TC according to approved RTCR Sample Siting Plan. | N/A
VANSANDT | No RMW | 11 | BRISTOL BAY LODGE / AK2261630 (46 / NC) |  |  | 1 |  |  | 1 | [17 empty] | Last sampled for Nitrate in 2018 and failed to submit RTCR Seasonal Start Up Procedures in 2019. System did not operate in 2020 due to COVID-19. | If operating in 2021, sample for Nitrate and submit RTCR Seasonal Start Up Procedures. | N/A
LITTLE | No RMW | 38 | CAMERON ACRES / AK2220473 (35 / C) | [6 empty] | 7 | [16 empty] | Exceeded the Arsenic MCL since 2017. | Install treatment to address the Arsenic MCL exceedance. | DEC received engineering submittal to address Arsenic exceedance using Point-of-Use devices. Conditional Construction Approval issued 08/18/2020, for Arsenic treatment system.
VANSANDT | BBAHC | 25 | CLARKS POINT WATER SYSTEM / AK2260202 (128 / C) | [5 empty] | 2 |  |  |  |  | 3 |  |  |  | 2 |  |  | 1 | 1 | 4 |  |  |  | Last sampled for annual Nitrate in 2017, periodic Arsenic in 2012, VOCs in 2014, IOCs in 2004, and last SOC waiver granted for 2014-2016 period. | Monitor for overdue regulated contaminants and submit an Initial SOC Monitoring Waiver for 2020-2022 period. | N/A
MORRISON | YKHC | 21 | CROOKED CREEK WATERING POINT / AK2280302 (147 / C) |  |  |  |  | 1 | [5 empty] | 7 |  |  |  |  | 6 | [7 empty] | Last sampled for TC with associated distribution chlorine residual in 2/2020, and annual DBPs in 2016. Overdue sanitary survey deficiencies from 2018 inspection. | Sample monthly TC and associated distribution system chlorine residual, sample for DBPs in 8/2021. Address sanitary survey deficiencies. | N/A
VANSANDT | No RMW | 20 | D & D RESTAURANT / AK2262660 (25 / NC) | [5 empty] | 2 |  |  |  |  | 8 | [12 empty] | Last sampled for Nitrate in 2017 and monthly TC in 11/2018. | When in operation, sample for Nitrate and TC. | N/A
VISSCHER | Maniilaq | 71 | DEERING UTILITY SYSTEM / AK2340222 (160 / C) | [7 empty] | 13 | [5 empty] | 1 | [9 empty] | Currently exceeding the MCL for TTHM, and has exceeded since 2017. Last sanitary survey completed in 2015. | Upgrade current treatment and have a sanitary survey completed. | Phase I of installing new direct filtration system with coagulation and pressure sand filters was constructed prior to DEC granting Approval to Construct. VSW received Phase II funding and are completing parts of Phase I that were not completed. Phase II will address corrosion control and DBPs. Work delayed due to COVID-19.
SHARP | NSHC | 19 | DIOMEDE JOINT UTILITIES / AK2340141 (184 / C) | [6 empty] | 2 | [7 empty] | 4 | 3 | [7 empty] | Currently exceeding RAA MCL for Arsenic and is performing required quarterly Tier 2 PN for MCL exceedances. New operator currently being trained and has begun submitting MORs. Due to COVID-19, NSHC personnel have not been able to travel to system. Overdue TTHM/HAA5 samples due to operational issues. | Install treatment to address historic Nitrate and Arsenic MCLs, submit a TTHM/HAA5 sample the 3rd quarter 2021, and quarterly Arsenic samples as soon as travel and logistics allow. | A PER was finalized. ANTHC's pilot study, anticipated in summer 2021, will include Ion Exchange technology and RO to help refine design of treatment plant upgrades. Also, plans to clean and paint the storage tank expected in summer of 2021. On 1/14/2021, DEC issued Construction Approval for new treated water WST to be operated in parallel with existing tank.
LATIMER | No RMW | 11 | DIRTY SKILLET AND BEAR CREEK CABINS / AK2242393 (54 / NC) | [5 empty] | 1 |  |  |  |  | 5 | [12 empty] | Last sampled for Nitrate in 06/2018 and TC in 08/2018. | Sample for Nitrate and TC in 2021. | N/A
VANSANDT | No RMW | 14 | EDDIES FIREPLACE INN / AK2261486 (64 / NC) | [10 empty] | 12 | [12 empty] | Last sampled for TC in 10/2019. | Sample for TC in 2021. | N/A
MORRISON | YKHC | 29 | EMMONAK WATER SYSTEM / AK2270299 (820 / C) |  |  | 1 |  |  |  |  | 3 | [7 empty] | 2 | 2 | [6 empty] | Overdue Level 2 Assessment sanitary defects from 2019 inspection. Failed to submit 2 OEL reports and has 3 TTHM MCL exceedances. Did not submit Lead/Copper samples in 2015, and submitted incomplete Lead/Copper set in 2018. | Address Level 2 Assessment sanitary defects, and submit missing OEL reports. Continue sampling quarterly DBPs and sample for Lead/Copper in 2021. | N/A
NAKANISHI | No RMW | 15 | FOREST PARK TC / AK2210794 (175 / C) |  |  |  |  | 1 | [13 empty] | 4 |  | 2 |  |  | Overdue sanitary survey deficiencies from 2019 inspection. Last sampled Well 2 for VOCs in 3rd quarter 2019 and Rads in 1st quarter 2020. | Address sanitary survey deficiencies. Communicate with DEC engineers regarding NOV. Resolve water pressure issues. Sample Well 2 for VOCs and Rads. | Distribution system unable to maintain ≥ 20 PSI due to unrepaired leaks.
NAKANISHI | No RMW | 21 | FOUR SEASONS TC / AK2210320 (365 / C) | [6 empty] | 4 | [16 empty] | Exceeded Arsenic MCL since 06/2019. | Install remediation or switch to city water. | N/A
VISSCHER | TCC | 22 | GALENA WTP1 - CITY / AK2360272 (470 / C) | [7 empty] | 4 | [8 empty] | 1 | [6 empty] | Currently exceeding the MCL for TTHM and HAA5, and has since 4th quarter 2019. Did not complete routine Lead/Copper monitoring in 2020 due to COVID-19. | Optimize or upgrade treatment system to limit DBP formation and increase TOC removal. Sample for Lead/Copper. | ANTHC is developing a new project to rehabilitate WTP1 controls and automation, change coagulants since current polymer is not effective, and expand coagulant testing to see if DBP precursor removal can be improved. In 01/2021, ANTHC and Galena decided on purchase of new conventional package WTP with dissolved air flotation process to help with DBP reduction. Approval to Construct WTP expected in 04/2021 and anticipate construction to start summer 2021.
LATIMER | No RMW | 12 | GEORGE INLET CANNERY / AK2121501 (129 / NC) |  |  | 1 |  |  | 1 |  |  |  |  | 1 | [12 empty] | System did not operate in 2020 due to COVID-19. | Sample for Nitrate and TC. | N/A
STATZ | YKHC | 113 | GRAYLING WATER SYSTEM / AK2280066 (195 / C) |  | 9 | [8 empty] | 3 |  | 18 |  |  | 1 | [7 empty] | Fails to consistently submit MORs, meet SWTR turbidity requirements (< 0.3 NTU), and complete monthly TC monitoring. Last sampled for E. coli (LT2) in 02/2018. | Begin monitoring for TC and E. coli (LT2). Also, submit a complete MOR with 95% of reported turbidity measurements at or below 0.3 NTU. | System is on a long-term BWN due to inadequate treatment. Reported broken flow meters in WTP.
BJORKMAN | DEC | 37 | HYDABURG / AK2120224 (415 / C) | [7 empty] | 7 | [15 empty] | Operator is working to increase flushing frequency. Hoping to see lower DBP levels in 02/2021. | Collect set of DBPs that allow the LRAA for HAA5 to be calculated below the MCL. | N/A
BJORKMAN | DEC | 42 | KAKE MUNICIPAL WATER / AK2130083 (415 / C) | [7 empty] | 8 | [15 empty] | Operator is working to increase flushing frequency and operational changes to lower DBP levels. | Collect set of DBPs that allow the LRAA for HAA5 to be calculated below the MCL. | N/A
VANSANDT | DEC | 11 | KARLUK WATER SYSTEM / AK2250087 (60 / C) |  |  |  | 1 | [13 empty] | 1 | [5 empty] | System does not meet SWTR due to lack of coagulant. Last sampled for IOCs in 2018, but considered incomplete because did not include Mercury. | Install filtration system with coagulant meeting SWTR. Sample for IOCs in 2021 that includes Mercury. | System does not meet SWTR due to lack of coagulant in the direct filtration units.
BJORKMAN | DEC | 37 | KLAWOCK / AK2120169 (904 / C) | [7 empty] | 7 | [15 empty] | Operator is working to increase flushing frequency. Hoping to see lower DBP levels in 03/2021. | Collect set of DBPs that allow the LRAA for HAA5 to be calculated below the MCL. | N/A
VISSCHER | No RMW | 99 | KOTZEBUE MUN. WATER SYSTEM / AK2340060 (3234 / C) | [7 empty] | 19 | [15 empty] | Currently exceeding the MCL for TTHM and HAA5, and have been for HAA5 since 2015 and TTHM since 2019. | Upgrade current treatment. | Plans for a new membrane filtration system, which will help reduce DBPs, received Construction Approval on 4/30/2020. WTP construction began summer 2020 and completion is expected for summer 2021.
STATZ | YKHC | 30 | KWETHLUK NEW PIPED WATER SYSTEM / AK2272017 (760 / C) |  | 1 | [5 empty] | 1 |  |  |  |  | 6 |  |  | 1 |  |  | 1 | 4 |  |  |  | Last sampled for quarterly TTHM and HAA5 in 07/2020, VOCs in 06/2020, and SOCs in 03/2016. Fails to consistently submit complete MORs and did not meet EP chlorine requirements in 08/2020. | Begin monitoring for the following contaminants: TTHM, HAA5, and VOCs. Submit an Initial SOC Monitoring Waiver for 2020-2022 period and submit a complete MOR. | N/A
STATZ | YKHC | 35 | KWIGILLINGOK WASHETERIA / AK2271700 (338 / C) | [5 empty] | 1 | [6 empty] | 18 |  |  | 7 |  |  | 1 |  |  |  |  | Last sampled for annual Nitrate in 10/2018, E. coli (LT2) in 07/2017, TTHM in 02/2013 and HAA5 in 10/2018, and VOCs in 10/2018. Last complete MOR submitted in 07/2019. | Begin monitoring for the following contaminants: Nitrate, E. coli (LT2), TTHM, HAA5, and VOCs. Also, submit a complete MOR. | On 10/2020, reported broken turbidimeter and pH meter.
VANSANDT | No RMW | 15 | L&PSD NEWHALEN SCHOOL / AK2260634 (73 / NTNC) |  |  |  |  | 2 | [18 empty] | Overdue sanitary survey deficiencies from 2015 inspection. | Address sanitary survey deficiencies. Specifically, work with DEC engineers on whether to apply for separation distance waiver, resolve with corrective action, or plan with timelines. | N/A
VANSANDT | BBAHC | 15 | MANOKOTAK HEIGHTS W/S / AK2262246 (215 / C) | [14 empty] | 1 |  | 2 | 1 | 1 | 4 | 1 |  |  | Last sampled for Arsenic in 2014, Lead/Copper in 2013, IOCs in 2008, VOCs in 2014, Rads in 2006. | Begin monitoring for the following contaminants: Arsenic, Lead/Copper, IOCs, VOCs. Submit an Initial SOC Monitoring Waiver for 2020-2022 period. | N/A
VANSANDT | BBAHC | 15 | MANOKOTAK WATER SYSTEM / AK2260090 (293 / C) |  |  |  |  | 1 | [9 empty] | 2 |  |  | 1 | 2 |  | 1 |  |  | Last sampled for Arsenic and VOCs in 2013, and cyclic Rads and Gross Alpha in 2006. System has overdue sanitary survey deficiencies (separation distance, well vent unscreened, no raw source water tap, and lack of proper well sanitary seal) from 2013 and 2017 inspections. | Sample for Arsenic, IOCs, VOCs, Rads. Address sanitary survey deficiencies. | N/A
GILLESPIE | No RMW | 16 | MEADOW BROOK SUBDIVISION / AK2220037 (465 / C) | [6 empty] | 3 | [15 empty] | 1 | System currently working with DEC engineers to add additional pumps to Well 5 in order to meet capacity. Intend to disconnect from Common Header that exceeds the Arsenic MCL. | Complete the modifications to Well 5 and disconnect the upper well house from the system. | N/A
MORRISON | YKHC | 12 | NAPAKIAK W.S. CENTRAL WELL / AK2262319 (330 / C) |  |  |  |  | 1 | [18 empty] | Overdue sanitary survey deficiencies from 2019 inspection. | Address sanitary survey deficiencies. | N/A
MORRISON | YKHC | 18 | NAPASKIAK WEST WATER SYSTEM / AK2260139 (200 / C) |  |  |  |  | 1 | [5 empty] | 9 |  |  |  |  | 2 | [5 empty] | 1 |  | Overdue sanitary survey deficiencies from 2017 inspection. Last sampled for TC and associated distribution system chlorine residual in 12/2019. Did not submit CCR certification page in 2019. | Address sanitary survey deficiencies. Sample TC and associated distribution system chlorine residual monthly, and submit 2019 CCR certification page. | N/A
MORRISON | YKHC | 29 | NATIVE VILLAGE OF SLEETMUTE / AK2271874 (82 / C) | [10 empty] | 1 |  | 18 |  |  | 4 | [5 empty] | 2 |  | Last sampled for TC and associated distribution system chlorine residual in 08/2020, annual DBPs in 2017, and has not completed LT2 sampling. System did not submit CCR certification form in 2019 or 2020. | Sample monthly for TC and associated distribution system chlorine residual, DBPs in 08/2021, and complete LT2 sampling. Submit CCR certification forms for 2019 and 2020. | N/A
MORRISON | YKHC | 34 | NEWTOK WATER SYSTEM / AK2271431 (435 / C) | [12 empty] | 21 |  |  | 5 |  |  | 3 |  |  | 1 |  | Last sampled for annual DBPs in 2014, VOCs in 2019, and has not completed LT2 sampling. System has been on long-term BWN since 2012 and reissued in 2017. | Sample for DBPs in 09/2021. Sample for E.coli (LT2) and VOCs in 2021. Submit MORs meeting monitoring and reporting requirements for turbidity and EP chlorine. | N/A
STATZ | YKHC | 53 | NIGHTMUTE NEW WATERING POINT / AK2271721 (243 / C) |  |  |  |  | 1 | 3 |  |  |  |  | 1 |  |  | 1 | 2 |  | 11 | 2 | 2 | 8 | 1 |  |  | Last sampled for TC in 08/2020, Nitrate in 03/2016, Arsenic in 01/2003, Lead/Copper in 02/2007, IOCs in 05/2003, VOCs in 12/2003, SOCs in 12/2003, Rads in 08/2007. Overdue sanitary survey deficiencies from 2019 inspection. Also, failed to collect a triggered source sample after TC+ result. | Begin monitoring for the following contaminants: TC, Nitrate, Arsenic, Lead/Copper, IOCs, VOCs, SOCs, Gross Alpha, combined Uranium, and combined Radium. Submit an Initial SOC Monitoring Waiver for 2020-2022 period. Address sanitary survey deficiencies. Also, collect a triggered source sample. | N/A
MORRISON | YKHC | 49 | NUNAM IQUA WATER SYSTEM / AK2270207 (213 / C) | [5 empty] | 1 |  |  |  |  | 6 |  | 32 |  |  | 3 | [7 empty] | Placed on BWN 08/26/2019 due to lack of TC sampling. Last sampled for TC in 03/2020, Nitrate in 2018, monthly TOC in 12/2019, missed DBP sampling in 2019, and has not completed LT2 sampling. Last MOR submitted in 08/2020. | Sample monthly for TC. In 2021, sample for Nitrate, TOC, quarterly DBPs in the 2nd month of the quarter, complete LT2 sampling, and submit MOR by the 10th of the following month. | N/A
VANSANDT | No RMW | 11 | OLDS RIVER INN / AK2250689 (85 / NC) | [5 empty] | 1 |  |  |  |  | 5 | [12 empty] | Last sampled for TC in 04/2020 and has not sampled for Nitrate. | Sample annual Nitrate, 1-Time Nitrite, and monthly TC during seasonal operations in 2021. Submit RTCR Sample Siting Plan. | N/A
MORRISON | YKHC | 32 | OSCARVILLE WATERING POINT / AK2270061 (75 / C) | [5 empty] | 1 |  |  |  |  | 9 |  |  |  | 1 | 1 | 4 | 1 | 1 |  | 2 | 3 |  | System has not sampled for any regulated contaminants or submitted a CCR since reactivation in 2018. | Install filtration/treatment. Sample for regulated contaminants and submit 2018-2020 CCRs. | No WTP to meet GU/SWTR requirements. Has been on long-term BWN since 04/2019.
VANSANDT | No RMW | 70 | PETER PAN SEAFOOD PORT MOLLER / AK2261216 (140 / NC) |  | 6 |  | 1 | [19 empty] | Not meeting effluent turbidity below 0.3 NTU. | Install filtration system that meets the SWTR requirements. Submit MORs meeting the turbidity and chlorine parameters and sample for E.coli (LT2) during seasonal operations. | Does not meet SWTR requirements due to lack of coagulation in direct filtration units and current system configuration.
MORRISON | YKHC | 115 | PLATINUM CITY WATER SYSTEM / AK2271059 (51 / C) |  |  |  | 1 |  | 4 |  |  |  |  | 28 |  | 18 |  |  |  | 17 | 1 | 4 | 8 | 1 | 8 |  | Last sampled for TC in 05/2018, Nitrate in 2014, VOCs in 2012, exceeded Lead/Copper in 2005, and has not submitted a RTCR Sample Siting Plan. | Monitor for regulated contaminants, install filtration/treatment, and submit RTCR Sample Siting Plan. | No WTP to meet GU/SWTR requirements. Has been on long-term BWN since 2014.
LITTLE | No RMW | 31 | QUIET CIRCLE APARTMENTS / AK2224476 (90 / C) | [6 empty] | 6 | [16 empty] | Exceeded Arsenic MCL with 1st quarter 2020 RAA compliance average of 0.011 mg/L. Placed on quarterly Arsenic monitoring in 2016. | Install treatment to address the Arsenic MCL exceedance. | Engineered treatment design is expected to be submitted to the DEC for constructional approval.
VANSANDT | No RMW | 11 | RAINBOW KING LODGE / AK2261606 (55 / NC) |  |  | 1 |  |  | 1 | [17 empty] | Last sampled for Nitrate in 07/2018 and did not submit RTCR Seasonal Start Up Procedures since 2018. System did not operate in 2020 due to COVID-19. | If operating in 2021, sample for Nitrate and TC. Submit RTCR Seasonal Start Up Procedures. | N/A
VANSANDT | No RMW | 11 | RAPIDS CAMP LODGE / AK2263025 (100 / NC) | [5 empty] | 1 |  |  |  |  | 3 | [12 empty] | Last sampled for Nitrate in 03/2018 and TC in 07/2019. System did not operate in 2020 due to COVID-19. | Sample for Nitrate and TC. | N/A
VANSANDT | No RMW | 20 | RENDEZVOUS / AK2250396 (56 / NC) |  |  |  |  | 1 | [5 empty] | 13 | [12 empty] | Last sampled for monthly TC in 08/2019. Overdue sanitary survey deficiencies from 2017 inspection. | If operational, sample for TC and address sanitary survey deficiencies. | N/A
VANSANDT | DEC | 36 | SAINT GEORGE WATER SYSTEM / AK2260074 (142 / C) | [5 empty] | 2 |  |  |  |  | 17 | [5 empty] | 2 |  | 2 |  |  |  |  | Last sampled for Nitrate in 2017, TC in 4/2019, Lead/Copper in 2006, and VOCs in 2012. | In 2021, sample for Nitrate, TC, Lead/Copper, and VOCs. | N/A
LATIMER | No RMW | 13 | SALMON CREEK TRAILER COURT / AK2241062 (125 / C) | [10 empty] | 9 | [10 empty] | 3 |  | Last sampled for TC in 12/2019 and has not submitted 2019 and 2020 CCR. | Sample for TC and submit 2019 and 2020 CCRs. | N/A
MORRISON | YKHC | 30 | SCAMMON BAY WATER SYSTEM / AK2270184 (484 / C) | [12 empty] | 21 |  |  | 2 | 1 | [6 empty] | Last sampled for HAA5 in 2017 and missed Lead/Copper in 2018. On BWN because untreated surface water is being used to prevent system freeze-up and meet community demand. Has not met EP chlorine residual monitoring requirements since 2018. | Sample for HAA5 in 10/2021 and Lead/Copper in 2021. Submit 3 satisfactory TC samples and resume treatment to rescind BWN. Monitor for EP chlorine residual every day (at or above 1.1 mg/L), and submit MORs by the 10th of the following month. | N/A
MORRISON | YKHC | 20 | SHAGELUK WATER SYSTEM / AK2280040 (60 / C) |  |  | 2 | [10 empty] | 1 |  | 5 | [7 empty] | Overdue Level 2 Assessment sanitary defects from 2016 inspection. Last sampled for DBPs in 2011 and failed to collect a triggered source sample after a TC+ result in 2019. | Address Level 2 Assessment sanitary defects. Sample for DBPs in 07/2021 and collect a triggered source sample. | N/A
GILLESPIE | No RMW | 39 | SNOWSHOE WATER SYSTEM / AK2223315 (180 / C) | [6 empty] | 7 | [7 empty] | 1 | [8 empty] | Currently exceeding the Arsenic MCL. Leaks are causing an increased demand on the system, forcing greater use of the high Arsenic source than was designed. | Reevaluate current process for addressing the Arsenic issue. | During summer of 2020, system identified and repaired additional leaks. However, those repairs intensified leaks elsewhere in the system. System is working to address this issue.
VANSANDT | No RMW | 17 | SOUTHEAST ALASKA LOGGING / AK2250427 (45 / NTNC) | [10 empty] | 1 |  | 11 |  |  | 1 | 2 |  | 1 |  |  |  |  | Last sampled for DBPs in 2008, Lead/Copper in 2016 and has not sampled for LT2. Fails to consistently submit MORs | Sample for E.coli (LT2), DBP2, Lead/Copper, and VOCs. Submit LT2 Sample Plan. Submit MOR by the 10th of the following month. | N/A
VANSANDT | No RMW | 11 | TAMARA'S CATERING & FOOD TRUCK / AK2263075 (30 / NC) | [5 empty] | 1 |  |  |  |  | 5 | [12 empty] | Last sampled for Nitrate and TC in 2018. | If operational in 2021, sample for Nitrate and TC. | N/A
BURG | DEC | 57 | TATITLEK WATER SYSTEM / AK2291130 (95 / C) | [7 empty] | 11 | [15 empty] | Currently exceeding HAA5 MCL. | Obtain a HAA5 LRAA below the MCL for two consecutive quarters. | Possible shortcut through storage tank that could be allowing HAA5's to form.
LATIMER | DEC | 14 | THORNE BAY, CITY OF / AK2120216 (470 / C) | [7 empty] | 2 | [7 empty] | 1 | 1 |  | 1 |  |  |  |  | System made progress on 2015 COBC to reduce DBP levels. Recent LRAA for TTHM was below MCL. Lab error issues for HAA5 4th quarter 2020 sample will delay meeting HAA5 MCL. | Continue to collect required DBP samples below the MCLs. | Received Interim Approval to Operate for modifications to the treatment system.
VANSANDT | No RMW | 16 | TIKCHIK NARROWS LODGE / AK2261648 (56 / NC) |  | 1 | [11 empty] | 1 | [9 empty] | System struggles to consistently meet SW turbidity and chlorine monitoring requirements. System did not operate in 2020 due to COVID-19. | When in operation, consistently submit monthly MORs with adequate chlorine and turbidity data. Also, have a sanitary survey sanitary survey completed in 2021. | N/A
MORRISON | YKHC | 24 | TULUKSAK WATER SYSTEM / AK2270223 (373 / C) |  |  |  |  | 1 | 1 | [9 empty] | 6 | 1 | [6 empty] | In 01/2021, BWN issued for the community because fire destroyed WTP. Last sampled for Nitrate in 2018, DBPs in 2016, and missed Lead/Copper in 2019. | Sample for Nitrate and Lead/Copper in 2021, and DBPs in 06/2021. | In 01/2021, the washeteria/watering point burned down destroying the WTP. Currently the community is using untreated surface water sources to meet community demand.
MORRISON | YKHC | 17 | TUNTUTULIAK WASHETERIA AND WATERING PT / AK2271211 (350 / C) |  |  |  |  | 1 |  |  |  | 1 | [7 empty] | 2 |  | 1 |  |  |  |  | Overdue sanitary survey deficiencies from 2017 inspection. Last sampled for VOCs in 2016. | Address sanitary survey deficiencies and sample for VOCs. | N/A
GARLAND | NSHC | 90 | UNALAKLEET CITY WATER SUPPLY / AK2340387 (757 / C) |  | 9 | [21 empty] | System struggles to meet SW turbidity requirements and placed in multiple BWNs in 2020. Treated water turbidimeter failed and has been temporarily replaced with the raw water turbidimeter. The failed turbidimeter has not yet been repaired or replaced. | Submit turbidity data indicating the treatment system is able to meet the turbidity limits on a continuous basis. EP and distribution chlorine residuals must also be included. | Filtration system routinely exceeds the turbidity treatment goals and sometimes the TT levels. Main issues are operational and equipment issues like aging pipes causing leaks. In 07/2020, DEC granted Construction Approval to WTP improvements to help with turbidity spikes during off-hours. Construction delayed due to COVID-19 but is expected to start summer 2021. Also, funding received for Phase II design for groundwater source that will not require microbial treatment. Design completion is expected in 04/2021, and construction to start summer 2021.
SHARP | NSHC | 11 | WALES WATER SYSTEM / AK2340191 (173 / C) | [9 empty] | 1 |  |  |  | 1 | [9 empty] | Currently exceeding RAA MCL for Uranium following the 2nd quarter 2020 results. Exceeded the RAA MCL intermittently since 2011. Last sanitary survey conducted in 2012. | Resolve the Uranium MCL and continue to monitor for Uranium. Have a sanitary survey completed in 2021. | Elevated Fluoride and Uranium in wells. On 12/2018, Construction Approval issued for new surface water source (infiltration gallery) and a cartridge filtration WTP. Project construction delayed due to COVID-19, so extension granted for two years. Construction expected to start summer 2021 and end summer 2022.
VANSANDT | No RMW | 24 | WINDMILL GRILLE / AK2262571 (85 / NC) |  |  |  |  | 1 | 2 |  |  |  |  | 7 | [12 empty] | Last sampled for Nitrate in 2017, TC in 6/2018. Overdue sanitary survey deficiencies from 2019 inspection. | When in operation, sample for Nitrate and TC. Address sanitary survey deficiencies. | N/A
BURG | No RMW | 11 | YAKUTAT LODGE / AK2130423 (30 / NC) |  |  | 1 | [7 empty] | 5 | [12 empty] | System receiving bottled water for consumption purposes due to PFAS contamination in well. | Sample monthly for TC and have a sanitary survey completed in 2021. | N/A

## Definitions
DW Program Staff Contact Information
Mat-Su = Office located in Wasilla, AK. Covers the Mat-Su area. Staff: Amy Hill (Program Coordinator) 376-1861, Tee Little (EPS) 376‐1860, Darryl Gillespie (EPS) 376-1824, Charity Bare (Engineering Supervisor) 262-3400
Northern = Office located in Fairbanks, AK. Covers the Northern Alaska PWSs. Staff: Marci Irwin (Program Coordinator) 451-2168, Karen Garland (EPS) 451‐2137, Teslyn Visscher (EPS) 451‐3038, Michael Sharp (EPS) 451-2178, Johnny Mendez (Engineering Supervisor) 451-5193
Southcentral / ANC= Office located in Anchorage, AK. Covers Anchorage bowl, Bethel/YK Delta, Dillingham area, Aleutian Chain, Pribilof and Kodiak Island area PWSs. Staff: Heather Murray (Program Coordinator) 269-7619, Elizabeth Nakanishi (EPS) 269‐7517, Darryl Stepien (EPS) 269‐7521, Leslie Morrison (EPS) 269-7518, Leah Van Sandt (EPS) 269-7653, Kalah Statz (EPS) 269-7647, Roy Robertson (Engineering Supervisor) 269‐7631. GENERAL ETT QUESTIONS: Jeanine Vance (EPM) 269-2007, Rachel Westbrook (EPS) 269‐7630, Kenna Billups (EPS) 269-8924
Kenai / Southeast = Office located in Soldotna, AK. Covers the Kenai Peninsula and Southeast area. Staff: Amy Hill (Program Coordinator) 376-1861, Eric Burg (EPS) 262‐3420, Jamie Bjorkman (EPS) 262‐3423, James Latimer (EPS) 262-3410, Charity Bare (Engineering Supervisor) 262-3400
Link to DW Program Directory (contact information) | http://dec.alaska.gov/eh/dw/contact/
Resource Links
Best Practices (BP) Score
The Best Practices (BP) Score is criteria for assessing operations and maintenance capacity of rural water and wastewater utilities. Used for determining eligibility and prioritization for community sanitation projects. STATEMENT FROM BP SCORE WEBSITE: The most effective way to increase a community's chance of receiving project funding is by improving their Best Practice score.
Link to BP Webpage | https://dec.alaska.gov/water/technical-assistance-and-financing/best-practices/
Alaska Community Database Online
The Community Database Online is a portal for information resources about Alaskan Communities and Places of Interest in an interactive format.
Link to Database Online Webpage | https://dcra-cdo-dcced.opendata.arcgis.com/
Alaska Community Photo Library
The Community Photo Library offers a glimpse into Alaska's communities and lifestyle by providing images of places, people, cultural events, public facilities, landscapes, and other dimensions of community life.
Link to Photo Library Webpage | https://www.commerce.alaska.gov/dcra/dcrarepoext/Pages/PhotoLibrary.aspx
Remote Maintenance Worker (RMW) Service Area Abbreviations
BBAHC= Bristol Bay area Health Corporation | Maniilaq= Maniilaq Health Corporation | TCC= Tanana Chiefs Conference
DEC= AK Department of Environmental Conservation | NSHC= Norton Sound Health Corporation | YKHC= Yukon Kuskokwim Health Corporation
No‐RMW= Not served by an RMW Program
Link to RMW Directory | http://dec.alaska.gov/media/21713/rmw-directory.pdf
Definitions
AL= Action Level | HAA5= Haloacetic Acids (Stage 1 Rule) | Rads= Radionuclides Rule
ANTHC= Alaska Native Tribal Health Consortium | IFE= Individual Filter Effluent | RMW= Remote Maintenance Worker
BACTI or t‐Coli = Total Coliform Sample | IOC= Inorganic Chemicals | RTC= Return to compliance (fall off ETT list)
BWN= Boil Water Notice | LCR= Lead/Copper Rule | RTCR= Revised Total Coliform Rule
CCR= Consumer Confidence Report | LRAA= Locational Running Annual Average (Stage 2) | SOC= Synthetic Organic Chemicals
CFE= Combined Filter Effluent | LT1= Long Term 1 Enhanced Surface Water Treatment Rule | Surface Water (SW)= Surface Water violations Surface Water Treatment Rules (SWTR, LT1, and LT2)
DPB= Disinfection by Products | LT2= Long Term 2 Enhanced Surface Water Treatment Rule
DSRD= Distribution Chlorine Residual | M/R= Monitoring and Reporting (type of violation) | TC= Total Coliform
EHO= Environmental Health Officer | MCL= Maximum Contaminant Level (type of violation) | TOC= Total Organic Carbon
EP= Entry Point | MOR= Monthly operator report | TCR= Total Coliform Rule (Also called Bacti)
EPA= Environmental Protection Agency | NOV= Notice of Violation | TT= Treatment Technique (violation)
EPRD= Entry Point Residual Distribution | OCC= Optimal corrosion control (Pb/Cu Rule) | TTHM= Total Trihalomethanes (Stage 1 Rule)
ETT= Enforcement Targeting Tool | PER= Preliminary Engineering Report | VOC= Volatile Organic Chemicals
FANLs= Facility Analyte Level (refers to SW/Stage 1 monitoring requirements) | PN= Public Notice | VSW= Village Safe Water
GAC= Granular Activated Carbon | PWS= Public Water System | WTP= Water Treatment Plant
GWUDI= Groundwater under the direct influence of surface water | RAA= Running Annual Average