## April 2024 ETT
April 2024 ETT List
Note: Column titled "Est. New ETT Score" is the estimated new score based on the violations that have Returned to Compliance (RTCd) during the Quarter. Please note that this score will likely change on the next quarter's list due to further violations being generated. Comments submitted by Drinking Water Program staff on April 29, 2024.
Staff | RMW | Est. New ETT Score | System Information | 10 Point |  |  |  | 5 Point | [7 empty] | 1 Point | [11 empty] | General Comments | How to Return to Compliance | Known Hardware Problems
|  |  |  | RTCR | SW | GWR | Nitrate | RTCR | SW | GWR | Nitrate | Arsenic | DBP | LCR | Rads | RTCR | SW | GWR | Arsenic | DBP | LCR | IOC | VOC | SOC | Rads | CCR | PN
EBERT | DEC | 20 | AKHIOK / AK2250037 (90 / C) | [7 empty] | 1 | [5 empty] | 10 |  |  | 1 | 1 |  | 1 |  |  | 1 |  | Last Nitrate, DBP, and VOC samples taken 2022. Last EPRD and turbidity sampling was June 2023. Lead Consumer Notices for 2022 samples are overdue for delivery. System did not submit CCR Certification form for 2022 CCR. | Collect Nitrate, DBP, and VOC samples. Collect monthly EPRD and turbidity samples and submit Monthly Operator Report. Deliver Lead Consumer Notices to consumers and DEC. Submit 2022 CCR Certification form. | N/A
EBERT | DEC | 16 | AKUTAN / AK2260252 (95 / C) | [7 empty] | 1 | [5 empty] | 8 |  |  | 1 |  |  | 1 |  |  |  |  | Last Nitrate, DBP, and VOC samples taken 2022. Last month with adequate LT2 sampling was May 2023. | Collect annual Nitrate, DBP, and VOC samples. Collect 2 LT2 samples each month. | N/A
NAKANISHI | YKHC | 86 | ALAKANUK WATER SYSTEM / AK2270362 (570 / C) | [7 empty] | 2 | [5 empty] | 32 |  |  | 33 | 1 |  | 5 |  |  |  |  | Nitrate, TOC (intake) and E.coli last taken in 2021. TOC (treated) and Alkalinity (intake) last taken in 2016. VOC's and DBP's last taken in 2015. full set of Lead & Copper last taken in 2012. Gross Alpha last taken in 2006 | Sample for Nitrate, TOC, ALK, E.coli, VOC's, DBP's, PbCu, and Gross Alpha. | None known
NAKANISHI | No RMW | 13 | ALASKA RAINBOW LODGE / AK2261680 (36 / NC) | [7 empty] | 1 |  |  |  |  | 7 | [11 empty] | Nitrate overdue as of 2023. Last TC sample taken June of 2022. | Sample for Nitrate and TC when system opens in 2023. | None known
BJORKMAN | No RMW | 18 | ALPINE INN / AK2244808 (30 / NC) | [7 empty] | 2 |  |  |  |  | 3 | [11 empty] | System is not open for the season until the end of May. Spoke with the operator 4/17 and they will submit SSUP, Nitrate, and TC before opening. | Collect a Nitrate and TC sample upon startup this season. | N/A
KEIM | Maniilaq | 11 | AMBLER COMMUNITY WATER SYSTEM / AK2300214 (261 / C) | [6 empty] | 1 | 1 | [16 empty] | System did not submit their annual 2023 Nitrate sample. The system also has an unresolved 2022 sanitary survey deficiency for failure to repair the water storage tank vent screen. | Collect a Nitrate sample as soon as possible in 2024. Submit photos of the repaired water storage tank vent screen, or submit an approvable corrective action plan and timeline to address this. | None known
LATIMER | DEC | 20 | ANGOON PUBLIC WATER / AK2130017 (450 / C) |  | 1 | [11 empty] | 5 |  |  | 3 | [6 empty] | 1 | System remains on BWN - for not meeting treatment, sampling, reporting, and op cert levels. Operator reports received for March/April include data for most, but not all days. Received TC results, but still no DS residuals. | Submit monthly reports on time to verify meeting treatment/filtration, collect monthly TC samples, and quarterly DBP samples. Continue working to meet operator certification requirements. | Parts/electrical work associated with use of inactive storage tank needs to be completed to reinstate use of ST to improve DS pressure.
CRIPPEN | YKHC | 20 | ANVIK WATER SYSTEM / AK2280171 (96 / C) | [7 empty] | 1 | [6 empty] | 1 | 1 | 5 | 1 | 1 | 1 |  |  |  |  | PWS has not monitored for annual DBPs since 2010. No IOC sample since 2010. Overdue for Nitrate, VOC and arsenic (cyclic schedule). System did not monitor for triggered source after TC positive sample in 2018. Lead consumer notice has not been returned to the state. | Sample for IOC, Nitrate, Arsenic and VOCs. Sample source for TC. Submit 2022 Lead Consumer Notice to DEC. Sample DBPs in July 2024. Address the outstanding corrective actions. | N/A
NAKANISHI | YKHC | 18 | ATMAUTLUAK WATER SYSTEM / AK2271033 (311 / C) | [7 empty] | 2 | [8 empty] | 2 |  |  | 2 |  |  |  |  | System last sampled for Nitrate and VOCs in 2021. System sampled last for DBPs in 2019 | Collect samples for Nitrate & VOC's ASAP. Collect annual DBP in December 2024. | None known
DAVIS | No RMW | 24 | BETHEL LONGHOUSE HOTEL / AK2270401 (90 / NC) | [6 empty] | 1 | 3 | [16 empty] | GWR VIO for no corrective actions from 2022 Sanitary Survey. No annual Nitrate since 2020. | CASS due date extended to 5/01/2024. Collect Nitrate. | N/A
SHARP | TCC | 73 | CHALKYITSIK VILLAGE WATER / AK2300183 (76 / C) | [9 empty] | 13 | [6 empty] | 5 | [7 empty] | System began exceeding the TTHM LRAA MCL during 4th quarter 2020 and continues to exceed. Has not completed an OEL report since 3rd quarter 2022. | System needs to optimize or upgrade treatment, including establishing and adhering to a GAC media change out schedule, to help reduce DBP formation. System also needs to complete overdue quarterly OEL report and submit updated public notice certification. | Adequate change out frequency will reduce chances of DBP exceedance. DEC received plans for a water treatment plant project. The project includes new winter/summer source intake, replacement WST, and modifications to the WTP, including CT contactor tanks to reduce chlorine needs; comments have been provided to engineer.
AGUE | YKHC | 12 | CHEVAK WATER SYSTEM / AK2270320 (938 / C) | [7 empty] | 2 | [9 empty] | 1 | [6 empty] | System has not collected a Nitrate sample since 2021 or Lead & Copper since 2019. | Collect a Nitrate sample ASAP. Complete Lead & Copper sample plan and collect 5 samples.
CRIPPEN | BBAHC | 28 | CHIGNIK LAKE WATER SYSTEM / AK2261096 (200 / C) | [6 empty] | 1 | 3 |  |  |  |  | 2 |  |  |  |  | 3 | [6 empty] | Last monitored for Nitrate in 2020. Last sampled for Lead & Copper samples (6 month sets) in 2019. The overdue survey corrective action (GWR vio) is for the booster station that was constructed and operated without ADEC engineering approval. ANTHC submitted a PER for review this spring and will be applying for funding that should address the booster pump station. | Monitor for Nitrate. Monitor for Lead & Copper. Collect monthly TC sample. Address the outstanding corrective action. | System is on a long term BWN due to consistent pressure/water loss.
NAKANISHI | YKHC | 17 | CHUATHBALUK WATER SYSTEM / AK2272012 (123 / C) | [7 empty] | 2 | [8 empty] | 2 | 1 |  | 1 |  |  |  |  | Overdue for Lead Consumer Notification, Nitrate, and VOC's as of 2022. Overdue for DBP's as of 2020. | Perform Lead Consumer Notification, sample for Nitrate and VOC's ASAP. Sample for DBP's in third quarter of 2024. | None known
CRIPPEN | YKHC | 12 | CITY OF HOOPER BAY / AK2270312 (1200 / C) | [7 empty] | 1 | [6 empty] | 1 |  | 1 | [7 empty] | Overdue for Nitrate and DBPs. EPS will continue to reach out to the system about consulting with the state regarding their most recent sanitary survey. | Collect Nitrate sample ASAP. Sample for DBPs between October and December 2024. Consult with the State regarding deficiencies, develop corrective action plan. | N/A
DAVIS | BBAHC | 42 | CLARKS POINT WATER SYSTEM / AK2260202 (128 / C) | [6 empty] | 1 | 5 | [7 empty] | 2 |  | 3 | 1 | 2 |  |  |  |  | Sanitary Survey deficiency (sink drain less than 100 ft., wellhead less than 12 inches) still unresolved. Overdue annual Nitrate and Lead/Copper samples. Overdue 3-year periodic Arsenic and VOCs samples. Last 9-year cyclic IOC sample was in 2004. | Address sanitary survey deficiencies: apply for separation distance waiver and extend wellhead to 12 inches above surface. Collect Nitrate, Arsenic, IOC and VOC samples. Collect 10 Lead & Cooper samples (10 samples required every 6-months schedule). Needs updated Lead/Copper plan. | N/A
HARRIS | No RMW | 16 | CLOVER PASS COMMUNITY CHURCH / AK2120575 (27 / NC) | [7 empty] | 1 |  |  |  |  | 10 | [11 empty] | Overdue for TC sample and MORs. PWS does not currently have a certified operator. Conversation with AC on 3/18/24 indicated system plans to disconnect rain catchment system from distribution system & purchase water for patron usage. PWS was informed of engineering submittal requirements, as well as continuation of DWP requirements until project completion. | Collect monthly TCR sample. Collect Nitrate sample. Complete/submit monthly operator report. Work with ADEC Op. Cert. Program to obtain required operator certification to operate a rain catchment PWS. | N/A
BJORKMAN | No RMW | 81 | CLOVER PASS RESORT / AK2120020 (133 / NC) |  | 8 | [22 empty] | System not open for 2024 season until mid May. | Submit an operator report with turbidity reading within parameters. | N/A
DAVIS | YKHC | 19 | CROOKED CREEK WATERING POINT / AK2280302 (147 / C) | [6 empty] | 1 | [9 empty] | 5 | 4 |  | 1 |  |  |  |  | Unresolved Corrective Actions from 2020 Sanitary Survey. No annual Lead/Copper (5 samples every 6 months) sample set collected since 2020. No DBPs collected since 2016. No VOCs collected since 2019. | Corrective significant deficiencies. Collect DBP and VOC samples. Received 1 Lead & Copper sample 3/11/24, need to collect 4 more samples to RTC violations. | N/A
HAKALA | Maniilaq | 53 | DEERING UTILITY SYSTEM / AK2340222 (160 / C) | [9 empty] | 8 |  |  |  | 6 |  |  | 1 | 3 | [6 empty] | PWS exceeds DBPs and missed 4th quarter 2023 DBP monitoring. Overdue for lead/copper monitoring, last sampling in December 2022, where they continued to exceed the 90th percentile action level for copper. They also have not submitted certification of lead consumer notification for the 2020 or 2022 sample sets. They have not submitted an operator report since September 2023. | Upgrade treatment system to control DBP formation, increase TOC removal, and address corrosion concerns. Collect all required samples, including 6-month lead/copper and quarterly DBP samples, and complete all public notice and reporting requirements. They must also collect daily chlorine/turbidity readings and report data on a monthly operator report. | System must upgrade their treatment system to control DBP formation, increase TOC removal, and address corrosion concerns. VSW received funding for Phase II WTP improvements to address corrosion control and DBPs.
SHARP | NSHC | 97 | DIOMEDE JOINT UTILITIES / AK2340141 (184 / C) |  |  |  | 1 |  |  |  | 1 | 12 |  |  |  |  | 9 |  | 7 |  | 1 |  | 1 |  |  |  |  | PWS exceeds the RAA MCL for Arsenic and Nitrate due to poor source quality. Missed 2023 Nitrate, Lead & Copper samples, and their 2022 & 2023 VOC samples, and are past due for arsenic monitoring since 2nd quarter 2022. They have also not submitted a complete monthly operator report since August 2023. | System needs to install treatment to address Nitrate, Arsenic, and SWTR. System will need to collect Nitrate, Lead & Copper, VOC, & Arsenic ASAP. | A new WTP is planned for installation to meet SWTR, Nitrate and Arsenic MCLs, and corrosion control. DEC granted construction approval. A temporary WTP is planned for operation early summer 2024 with WTP construction completion expected late summer 2024. Storage tank is reported to have some internal corrosion and sediment build-up that may be contributing to water quality issues.
EBERT | YKHC | 21 | EEK WATER SYSTEM / AK2270281 (280 / C) | [7 empty] | 2 | [8 empty] | 2 | 5 |  | 2 |  |  |  |  | Last Lead/Copper, Nitrate, DBP, and VOC samples taken 2021. | Collect 10 Lead/Copper samples for 6 month period. Collect Nitrate, DBP, and VOC samples. | N/A
NAKANISHI | No RMW | 19 | FOREST PARK TC / AK2210794 (175 / C) | [6 empty] | 2 | [12 empty] | 2 |  | 2 |  |  | Sanitary Survey deficiencies (GWR) are from the 2016 and 2019 surveys, system reportedly does not have the financial capacity to address the deficiencies. | System must submit engineering plans to correct deficiencies. System must sample their east well for VOC's and RAD's | None known
SHARP | NSHC | 25 | GOLOVIN COMMUNITY WATER SYSTEM / AK2340214 (150 / C) | [9 empty] | 4 |  |  |  | 1 |  |  | 3 | [7 empty] | System has an outstanding turbidity violation for not submitting filter performance questions (page 3) with July 2023 operator report. They cannot RTC until they pump again. Exceeds the LRAA for HAA5, overdue for OEL Reports. | System needs to adjust treatment to continue to reduce HAA5 levels, submit quarterly OEL reports, and submit filter performance information with the monthly operator report during next pumping period. | During inspection of system in August 2023, operator could not fill storage tank because raw water turbidity was too high for the treatment system to remove it. They may need to schedule tank filling during less turbid periods in summer or devise a way to reduce the raw water turbidity.
CRIPPEN | YKHC | 221 | GRAYLING WATER SYSTEM / AK2280066 (195 / C) | 2 | 7 |  |  | 1 |  |  | 1 |  |  |  |  | 5 | 97 |  |  | 7 | 5 |  | 1 |  |  |  | 2 | PWS struggles to consistently meet SW turbidity monitoring requirements. Last sampled for E. coli (LT2) in 2018, DBPs in 2020, Lead/Copper in 2019. PWS has an outstanding Tier 2 Public Notice and certification due back to DEC. | Submit a completed MOR that meets SWTR requirements. Sample for E. coli (LT2), DBPs, and Lead & Copper. Collect monthly TC sample. Submit public notice and public notice certification. | System on long-term BWN due to inadequate treatment. Storage tank is aged and too small to meet community needs. Distribution loop is leaking. Work is currently being done on the sand filters and lift station, once complete they should be starting up.
ROBERTS | DEC | 26 | GULKANA VILLAGE / AK2380214 (90 / C) | [9 empty] | 5 | [14 empty] | System has been exceeding the TTHM LRAA MCL since 4th quarter 2022. | System must optimize their treatment system to limit DBP formation and increase TOC removal. System will RTC once TTHM LRAA is below the MCL. | A new WST is planned for construction in 2024 and will replace the existing WST; CA granted. Tank piping will be designed to reduce thermal stratification; this could reduce water age in tank and help with reduction in DBP formation. Temporary tanks will be installed while construction of the new tank is underway.
NAKANISHI | No RMW | 14 | HEART OF THE SHIRE / AK2263061 (79 / NC) | [6 empty] | 1 | 1 |  |  |  |  | 1 | [11 empty] | Nitrate overdue as of 2023. RTCR Sample Siting Plan was due by 5/22/2020. System has overdue significant deficiency that was due by 2/10/2022. Unable to contact system - seasonal | Sample for Nitrate, submit an RTCR Sample siting plan, and work with DEC on Significant deficiency. | None known
SHARP | TCC | 11 | HUGHES PUBLIC WATER SUPPLY / AK2300272 (107 / C) | [13 empty] | 6 |  |  |  | 1 | [6 empty] | System did not submit certification of lead consumer notification for 2022 Lead & Copper sample set and has not submitted a completed MOR without issues since August 2023. | System must submit a complete operator report without turbidity or chlorine issues and send in certification of lead consumer notification for both 2022 and 2023 sample sets. | ANTHC submitted FATO request in Dec. 2023 for the WTP and WST projects. ANTHC is planning to make future changes to the WST to improve chlorine contact time.
EBERT | No RMW | 11 | JAVA FLATS/RUSSIAN RIVER ROADHOUSE / AK2250582 (39 / NC) | [7 empty] | 2 | [16 empty] | Last Nitrate sample taken 2021. | Collect annual Nitrate sample. | N/A
LATIMER | No RMW | 15 | JERSEY SUBS KASILOF / AK2249994 (42 / NC) |  |  |  |  | 1 |  |  | 1 |  |  |  |  | 5 | [11 empty] | Overdue Nitrate, TC sample, and seasonal startup. PWS owner/operator has not been responsive thus far to emails and voice msgs during 2023-2024. | Startup needs to be completed w/ SSUP form submitted on time, collect Nitrate and TC samples in first month of 2024 season. | N/A
DAVIS | YKHC | 15 | KIPNUK WATER SYSTEM / AK2270736 (639 / C) | [7 empty] | 1 | [5 empty] | 1 |  |  | 6 |  |  | 1 |  |  |  |  | No annual Nitrate and VOCs collected since 2022. No Lead & Copper samples collected since 2020. | Collect annual Nitrate, VOCS and 3 yr. 10 sample set Lead & Copper. | N/A
ROBERTS | Maniilaq | 91 | KIVALINA WATER SYSTEM / AK2340117 (452 / C) |  | 9 | [22 empty] | January, April, and June-December 2023 TT violations for not meeting entry point chlorine requirements remain valid. | System must ensure they are chlorinating appropriately to meet SW treatment rules and submit complete monthly operator reports. | New direct filtration and GAC WTP construction approval issued August 2023. Construction was delayed to 2024 with start-up planned for 2025.
BJORKMAN | DEC | 99 | KLAWOCK / AK2120169 (904 / C) | [9 empty] | 19 | [14 empty] | PWS exceeding HAA5 MCL. System is looking into modifications/ upgrades and have projects in process with ANTHC. This includes the installation of a PAX mixer to be installed. | Collect a set of DBP samples that allow for the LRAA for HAA5 to be calculated below the MCL. | Need to install Pax mixer. The mixer was delayed and they recently discussed approval requirements with DEC Engineering for installation. The system was instructed to wait until the tank repairs are made (currently waiting on engineering plan submittal).
AGUE | DEC | 14 | KOKHANOK WATER & WW SYSTEM / AK2263006 (189 / C) | [12 empty] | 2 | 1 |  |  | 1 | 4 |  | 2 |  |  |  |  | System overdue for TC sampling since October 2023, Lead & Copper since 2022, and VOCs since 2022. | Collect a TC sample ASAP. Collect 2 annual 6-month Lead & copper sample sets in 2024 and an annual VOC sample. | New WTP under construction will correct open deficiencies identified in 2021 sanitary survey. Project expected to be completed summer 2024.
NAKANISHI | YKHC | 14 | KOTLIK WATER SYSTEM / AK2272004 (617 / C) | [9 empty] | 2 | [9 empty] | 1 |  |  |  |  | VOC overdue as of 2023. | Sample for VOC's, and resolve TOC % Removal issues. | None known
SHARP | No RMW | 99 | KOTZEBUE MUN. WATER SYSTEM / AK2340060 (3234 / C) | [9 empty] | 19 | [14 empty] | PWS has exceeded the TTHM MCL since 2019 and the HAA5 LRAA since 3rd quarter 2023. | The new ultrafiltration-nanofiltration membrane treatment system began its operation in December 2022, however, the system is still experiencing high DBPs. System needs to optimize their treatment system to reduce the DBP LRAA levels below the MCL. | Monitoring and adjustments of new WTP continue and DBP levels are expected to improve. DBP precursor removal data is being analyzed to determine what adjustments to treatment are necessary to improve DBP results. The system is actively working to resolve the treatment issues.
EBERT | No RMW | 29 | KSD ANIAK SECONDARY SCHOOL / AK2271732 (80 / NTNC) | [7 empty] | 3 |  |  | 1 | [6 empty] | 3 |  | 1 |  |  |  | 2 | Public notification and public education requirements following Lead/Copper exceedance are overdue. Lead Consumer Notices for 2022 samples are overdue. Last Lead/Copper sample taken 2022. Last Nitrate sample taken 2020. Last VOC sample taken 2019. | Complete the public notification and education requirements. Deliver the 2022 Lead Consumer Notices to consumers and DEC. Collect 10 Lead/Copper samples for 6 month period. Collect Nitrate and VOC samples. | N/A
EBERT | No RMW | 18 | KSD GEORGE MORGAN HIGH SCHOOL / AK2270833 (50 / NTNC) |  |  |  |  | 1 |  |  | 2 | [6 empty] | 1 |  |  |  |  | 1 |  |  |  |  | Repeat TC samples were not completed for TC positive sample taken 5/17/2022. System is overdue to submit Level 1 Assessment by 6/30/2022. Last Nitrate sample taken 2021. Last VOC sample taken 2019. | Collect repeat TC samples. Submit Level 1 Assessment. Collect Nitrate sample, and a VOC sample. | N/A
EBERT | No RMW | 15 | KSD UPPER KALSKAG PRIMARY SCHOOL / AK2272751 (50 / NTNC) | [7 empty] | 2 | [9 empty] | 1 | 1 | 2 |  |  |  |  | Last Nitrate and VOC samples taken 2021. Last Chromium sample and last full set of 5 Lead/Copper samples taken 2019. | Collect Nitrate, VOC, and IOC (including Chromium) samples Collect set of 5 Lead/Copper samples. | N/A
AGUE | YKHC | 15 | KWETHLUK NEW PIPED WATER SYSTEM / AK2272017 (760 / C) | [7 empty] | 1 | [8 empty] | 3 | 2 |  | 1 |  |  |  |  | System is overdue for Nitrate, Lead & Copper, and VOC sampling. Quarterly DBPs not collected since January 2023. Several DBP and TOC samples collected in late 2023 could not be analyzed due shipping delays which caused hold time and temperature problems. | Collect a Nitrate sample ASAP and monitor for DBPs and VOCs. Develop Lead & Copper sample plan and collect an annual sample set. | NA
EBERT | YKHC | 78 | KWIGILLINGOK WASHETERIA / AK2271700 (400 / C) | [7 empty] | 2 | [5 empty] | 55 |  |  | 6 | 1 |  | 2 |  |  |  |  | Last LT2 samples taken in July 2017. Last VOC, Nitrate, and HAA5 samples taken 2021. Last TTHM sample taken 2014. Last Lead/Copper sample taken 2017. | Collect LT2 samples when making water. Collect VOC, Nitrate, and DBP (HAA5 and TTHM) samples. Collect set of 5 Lead/Copper samples . | N/A
NAKANISHI | No RMW | 13 | LKSD TUNUNAK PAUL ALBERT HS / AK2270613 (385 / C) | [7 empty] | 1 | [8 empty] | 3 |  |  | 3 |  |  |  |  | VOC's and DBP's overdue as of 2021. Nitrate overdue as of 2023. | Sample for Nitrate, VOC's, and DBP's | None known
AGUE | YKHC | 11 | LOWER KALSKAG WATER SYSTEM / AK2270697 (302 / C) | [6 empty] | 1 | [10 empty] | 1 | [6 empty] | System did not distribute lead consumer notices following 2022 sampling and has outstanding significant deficiencies from their 2023 sanitary survey. | Distribute consumer notices and correct significant deficiencies. | System has open significant deficiencies regarding drainage and screening of the wells and cross connections in the treatment plant.
EBERT | BBAHC | 12 | MANOKOTAK HEIGHTS W/S / AK2262246 (215 / C) | [20 empty] | 7 |  |  |  | System did not submit an SOC monitoring waiver application for 2020-2022. | Submit SOC waiver application for 2023-2025 or collect quarterly SOC samples. | N/A
NAKANISHI | YKHC | 37 | MERTARVIK WATER SYSTEM / AK2272756 (170 / C) | [7 empty] | 3 |  |  |  |  | 2 | [8 empty] | 16 |  |  | Overdue for Nitrate and Rads since 2020. No Routine TC samples collected since October 2023 (special purpose TC samples collected February 2024 to come off of boil water notice). | Sample for Nitrate, RADS, and Total Coliform | None known
AGUE | YKHC | 14 | MOUNTAIN VILLAGE WATER SYSTEM / AK2270150 (850 / C) | [6 empty] | 1 | 1 | [7 empty] | 1 | 1 |  | 1 | [5 empty] | System is overdue for annual Nitrate and DBP sampling, and missed previous 3 year cycle sample for Arsenic and IOCs. There are open significant deficiencies from 2022 sanitary survey | Collect Nitrate, DBP, arsenic, and IOC samples ASAP. Correct significant deficiencies. | System has ongoing issues producing enough water to meet community demand with their current wells, and is using river water as a primary source at this time. System is on boil water notice due to use of unapproved source.
DAVIS | YKHC | 12 | NAPAKIAK W.S. CENTRAL WELL / AK2262319 (330 / C) | [6 empty] | 1 | [7 empty] | 1 |  | 1 | [7 empty] | PWS has violations from sanitary survey conducted 4/18/2022 due to unresolved deficiencies. No 3-yr. DBP2 collected since 2020. | Consult with DEC regarding significant deficiencies (NSF hose to fill chem. tank, air gaps, water haul trailer), and address CASS. Collect DBP samples. | N/A
NAKANISHI | YKHC | 15 | NAPASKIAK WEST WATER SYSTEM / AK2260139 (200 / C) | [6 empty] | 1 | 1 | [8 empty] | 1 | [7 empty] | PWS has unresolved Sig deficiencies 2018 & 2022 Sanitary surveys. Nitrate and DBP samples overdue as of 2023 | Work with DEC to correct Significant Deficiencies, sample for Nitrate and DBP's | None known
DAVIS | DEC | 14 | NELSON LAGOON WATER SYSTEM / AK2260804 (60 / C) | [7 empty] | 1 | [8 empty] | 3 |  |  | 3 |  |  |  |  | No annual Nitrate collected since 2022. No annual VOCs collected since 2020. No annual TTHM collected since 2021, and no annual HAA5 collected since 2022. | Collect Nitrate, TTHM, HAA5 and VOC samples. | N/A
NAKANISHI | YKHC | 58 | NEWTOK WATER SYSTEM / AK2271431 (435 / C) | [7 empty] | 2 |  | 4 |  |  |  | 9 |  |  | 10 | 1 |  | 2 | 4 |  |  |  | Nitrate, VOC and DBP's last taken in 2021. PbCu last taken in 2019. LT2 sample last taken 2020. | Sample for Nitrate, DBPs, LT2, LCR, VOCs and submit an SOC waiver application | Village is being relocated to another city due to land erosion. Source water has been contaminated with sea water and has high TDS.
AGUE | YKHC | 34 | NIGHTMUTE NEW WATERING POINT / AK2271721 (243 / C) |  |  |  |  | 1 |  | 1 | 1 | [9 empty] | 14 | [6 empty] | Did not collect an annual Nitrate sample in 2023, and has not sampled for lead & copper since 2007. System has outstanding significant deficiencies from 2022 survey and open sanitary defects from 2022 Level 1 Assessment. | Collect Nitrate and lead & copper samples ASAP. Correct significant deficiencies and sanitary defects. | The system does not have a raw water sample tap and does not have appropriate backflow prevention at the watering point. RMW trip required to correct these sanitary defects/significant deficiencies.
DAVIS | DEC | 19 | NONDALTON / AK2260260 (205 / C) | [7 empty] | 1 | [8 empty] | 3 | 2 |  | 3 | 4 |  |  |  | No annual Nitrate collected in 2023. No DBP2, and VOCs sampled since 2020, and Lead & Copper since 2015. 2023-2025 SOC waiver application has not been received. | Collect Nitrate, DBP2 (collect in August 2024), VOCs, and Lead/Copper samples. Submit 2023-2025 SOC waiver to DEC. | N/A
NAKANISHI | YKHC | 36 | NUNAM IQUA WATER SYSTEM / AK2270207 (213 / C) | [9 empty] | 5 |  |  | 2 | 4 |  |  | 1 | [7 empty] | TOC % removal RAA not met since 2021. | Continue to sample for TC, DBP's and TOC/Alkalinity as required. | None known
DAVIS | DEC | 47 | OLD HARBOR / AK2250061 (246 / C) |  | 1 | [5 empty] | 3 | [8 empty] | 7 | 8 |  | 3 |  |  |  |  | SW TT violation for not meeting EPRD requirements. Last annual Nitrate, DBPs, and VOCs sampled in 2020. Last Lead/Copper sample set (10 samples every 6 months) collected in 2022. | Report consistent EPRD readings at the required levels. Sample for Nitrate, VOC, and DBP2 (August 2024). Monitor Lead/Copper every six-months (10 samples/set). | N/A
DAVIS | No RMW | 11 | PETER PAN SEAFOOD PORT MOLLER / AK2261216 (140 / NC) | [5 empty] | 1 | [6 empty] | 1 | [11 empty] | Routine monthly TC not collected during last month of operation 8/2023. Seasonal TNC system not meeting the SWTR due to current system configuration and lack of coagulation. | Collect monthly TC during 1st month of operation. Install filtration system that meets the SWTR requirements. | System does not meet SWTR due to lack of coagulant in their filtration units.
NAKANISHI | No RMW | 12 | PETERS CREEK TERRACE / AK2211473 (70 / C) | [6 empty] | 1 | [10 empty] | 1 |  |  |  |  | 3 |  | Significant deficiency corrective action overdue as of 10/23/2023, no CCR submitted in 2022 or 2023, PbCu sample were due to be taken in 2020. | Collect Lead & Copper sample set, submit CCR report, and correct signification deficiency for drainage. | None known
EBERT | YKHC | 83 | PLATINUM CITY WATER SYSTEM / AK2271059 (51 / C) | [5 empty] | 1 |  | 2 |  |  |  |  | 19 |  |  |  |  | 23 | 1 | 5 | 7 |  | 8 |  | System does not meet applicable water treatment and filtration requirements. CCR certification forms were not submitted 2016-2022. RTCR Sample Siting Plan is overdue. Last routine TC sample taken 6/7/2022. System doesn't have current SOC monitoring waiver or samples. Last Nitrate sample taken 2021, last VOC 2012, last Lead/Copper 2005, and last IOC sample taken 2005. | Install applicable water treatment and filtration. Submit 2022 CCR certification form. Submit an RTCR Sample Siting Plan. Collect monthly routine TC samples. Submit an initial SOC waiver application for 2023-2025 or collect quarterly SOC samples. Collect Nitrate, VOC, Lead/Copper (5 samples for 6 month period), and IOC samples. | System does not meet applicable water treatment and filtration requirements.
HARRIS | DEC | 32 | PORT PROTECTION / AK2121123 (60 / C) | 2 |  |  |  | 1 | 1 | [18 empty] | System classified as a GWUDISW and has not installed filtration/ disinfection. Has not completed all RTCR Assessments triggered by TC+/EC+ sampling. System submitted plans to perform source infiltration gallery upgrades in 2024 to improve testing results. | Install filtration & disinfection treatment system. Hire third-party surveyor to perform Level 2 Assessment. | System is on a long-term BWN due to lack of treatment & repeated TC+/EC+ results. Source water infiltration gallery currently intaking raw water & substrate deposits from creek.
NAKANISHI | No RMW | 41 | RED DOG INN / AK2260749 (145 / NC) | [7 empty] | 4 |  |  |  |  | 18 | [11 empty] | Nitrate overdue since 2020. TC overdue since July 2022. | Sample for Nitrate and Total Coliform | System pipes were frozen as of December 2023. System inactive until repairs are completed.
AGUE | YKHC | 32 | SHAGELUK WATER SYSTEM / AK2280040 (60 / C) |  |  |  |  | 1 |  |  | 2 |  |  |  |  | 1 |  | 2 |  | 6 | 3 |  | 1 |  |  |  |  | System has not collected DBP samples since 2011 and has not conducted sufficient follow-up sampling after a copper action level exceedance in 2016. VOCs were not collected during last monitoring period. Monthly chlorine reports and last 2 annual Nitrate samples not collected. | Collect Nitrate, DBP, lead & copper, and VOC samples. Submit monthly chlorine reports and collect monthly TC samples consistently. | Sanitary defect for improper well seal identified in 2016 remains open.
BJORKMAN | No RMW | 22 | SILVERKING LODGE / AK2121463 (46 / NC) |  | 2 | [11 empty] | 2 | [10 empty] | System not open for 2024 season until mid May. | Submit an operator report with turbidity reading within parameters. | N/A
DAVIS | No RMW | 14 | SOUTHEAST ALASKA LOGGING / AK2250427 (45 / NTNC) | [7 empty] | 1 | [8 empty] | 1 |  |  | 1 | 4 |  |  |  | No annual Nitrate, TTHM & HAA5, VOCs collected since 2022. | Collect annual Nitrate, TTHM, HAA5 and VOCs ASAP. SOC waiver approval for 2023-2025 period, waiver application has been submitted and is under review. | n/a
KEIM | DEC | 14 | TAKOTNA WATER SYSTEM / AK2280163 (70 / C) | [12 empty] | 4 | 7 |  |  | 1 | 1 | [6 empty] | System has been on a Boil Water Notice since 9/18/23 due to a failure of their generators which resulted in frequent loss of power/pressure issues. Overdue for monthly TC samples, monthly operator reports, and missed their 2023 Lead & Copper samples. | System must begin submitting routine monthly TC samples and complete monthly operator reports. They also must submit a set of Lead & Copper samples. | Systems generator was failing fall 2023 which resulted in frequent loss of power/pressure issues.
HARRIS | DEC | 94 | TATITLEK WATER SYSTEM / AK2291130 (95 / C) | [9 empty] | 18 | [14 empty] | System has ongoing DBP exceedances since 2015. System still exceeding Lead. Faucet replacement has not been completed. System to develop & implement a line flushing program. | Install treatment to reduce DBP's. Replace faucets where Lead is exceeding. | High Lead levels in distribution system. Chlorine injection equipment likely not operating smoothly.
AGUE | YKHC | 42 | TUNTUTULIAK WASHETERIA AND WATERING PT / AK2271211 (350 / C) |  |  |  |  | 1 |  | 2 |  |  |  | 1 |  | 6 |  | 1 | 3 |  | 6 |  |  |  |  | 1 |  | System had a Lead AL exceedance in 2016 and has not completed follow up sampling. System overdue for Arsenic sample. Monthly TC samples not collected since June 2023, when a Level 1 Assessment was triggered and not completed. | Collect Lead & Copper, Arsenic, and TC samples ASAP. Address significant deficiencies and certify that the CCR is distributed in 2024. | System is on a long-term BWN due to open significant deficiencies and failure to sample consistently.
EBERT | No RMW | 13 | VFW KODIAK POST #7056 / AK2250493 (46 / NC) | [7 empty] | 1 |  |  |  |  | 3 | 5 | [10 empty] | Last TC sample taken 9/12/2023. Last EPRD and turbidity sampling was July 2023. Last Nitrate sample taken 2022. | Collect monthly TC sample. Collect monthly EPRD and turbidity samples and submit Monthly Operator Report. Collect Nitrate sample. | N/A
SHARP | NSHC | 38 | WALES WATER SYSTEM / AK2340191 (173 / C) | [11 empty] | 7 | [12 empty] | System exceeds the RAA MCL for Uranium. | New source and WTP project to address Uranium MCL is currently in progress. Must be completed in order to reduce Uranium levels. | Source wells have elevated fluoride and uranium. CA issued in Dec. 2018 for new surface water source (infiltration gallery) and a cartridge filtration WTP. Construction was delayed, but has now been mostly complete; waiting till summer 2024 to commission.

## Definitions
DW Program Staff Contact Information
Mat-Su = Office located in Wasilla, AK. Covers the Mat-Su area. Staff: Amy Hill (Program Coordinator) 376-1861, Vacant (EPS) 269-7584, Jessica Cahill (EPS) 376-1824, Charity Bare (Engineering Supervisor) 262-3400
Northern = Office located in Fairbanks, AK. Covers the Northern Alaska PWSs. Staff: Teslyn Hakala (Program Coordinator) 451-3038, Michael Sharp (EPS) 451-2178, Jenny Roberts (EPS) 451‐2137, Gretchen Keim (EPS)451-2231, Johnny Mendez (Engineering Supervisor) 451-5193
Southcentral / ANC= Office located in Anchorage, AK. Covers Anchorage bowl, Bethel/YK Delta, Dillingham area, Aleutian Chain, Pribilof and Kodiak Island area PWSs. Staff: Heather Murray (Program Coordinator) 269-7619, Elizabeth Nakanishi (EPS) 269‐7517, Kristine Crippen (EPS) 269‐7521, Jordan Ebert (EPS) 269-3068, Monica Ague (EPS) 269-7653, John Davis (EPS) 262-8201, Chris Pletnikoff (Engineering Supervisor) 269‐6064.
Kenai / Southeast = Office located in Soldotna, AK. Covers the Kenai Peninsula and Southeast area. Staff: Amy Hill (Program Coordinator) 376-1861, Jamie Bjorkman (EPS) 262‐3423, James Latimer (EPS) 262-3410, Christina Harris (EPS) 262-3420, Charity Bare (Engineering Supervisor) 262-3400
GENERAL ETT QUESTIONS: Jeanine Vance (EPM) 269-2007, Karen Garland (EPS) 269-7576, Eric Burg (EPS) 262-3401
Link to DW Program Directory (contact information) | http://dec.alaska.gov/eh/dw/contact/
Resource Links
Best Practices (BP) Score
The Best Practices (BP) Score is criteria for assessing operations and maintenance capacity of rural water and wastewater utilities. Used for determining eligibility and prioritization for community sanitation projects. STATEMENT FROM BP SCORE WEBSITE: The most effective way to increase a community's chance of receiving project funding is by improving their Best Practice score.
Link to BP Webpage | https://dec.alaska.gov/water/technical-assistance-and-financing/best-practices/
Alaska Community Database Online
The Community Database Online is a portal for information resources about Alaskan Communities and Places of Interest in an interactive format.
Link to Database Online Webpage | https://dcra-cdo-dcced.opendata.arcgis.com/
Alaska Community Photo Library
The Community Photo Library offers a glimpse into Alaska's communities and lifestyle by providing images of places, people, cultural events, public facilities, landscapes, and other dimensions of community life.
Link to Photo Library Webpage | https://www.commerce.alaska.gov/dcra/admin/Photo
Remote Maintenance Worker (RMW) Service Area Abbreviations
BBAHC= Bristol Bay area Health Corporation | Maniilaq= Maniilaq Health Corporation | TCC= Tanana Chiefs Conference
DEC= AK Department of Environmental Conservation | NSHC= Norton Sound Health Corporation | YKHC= Yukon Kuskokwim Health Corporation
No‐RMW= Not served by an RMW Program
Link to RMW Directory | https://dec.alaska.gov/media/p4dntxhf/rmw-directory.pdf
Definitions
AL= Action Level | HAA5= Haloacetic Acids (Stage 1 Rule) | RAA= Running Annual Average
ANTHC= Alaska Native Tribal Health Consortium | IFE= Individual Filter Effluent | Rads= Radionuclides Rule
BACTI or t‐Coli = Total Coliform Sample | IOC= Inorganic Chemicals | RMW= Remote Maintenance Worker
BWN= Boil Water Notice | LCR= Lead/Copper Rule | RTC= Return to compliance (fall off ETT list)
CCR= Consumer Confidence Report | LRAA= Locational Running Annual Average (Stage 2) | RTCR= Revised Total Coliform Rule
CFE= Combined Filter Effluent | LT1= Long Term 1 Enhanced Surface Water Treatment Rule | SOC= Synthetic Organic Chemicals
DPB= Disinfection by Products | LT2= Long Term 2 Enhanced Surface Water Treatment Rule | Surface Water (SW)= Surface Water violations Surface Water Treatment Rules (SWTR, LT1, and LT2)
DSRD= Distribution Chlorine Residual | M/R= Monitoring and Reporting (type of violation)
EHO= Environmental Health Officer | MCL= Maximum Contaminant Level (type of violation) | TC= Total Coliform (also called Bacti)
EP= Entry Point | MOR= Monthly operator report | TOC= Total Organic Carbon
EPA= Environmental Protection Agency | NOV= Notice of Violation | TCR= Total Coliform Rule
EPRD= Entry Point Residual Distribution | OCC= Optimal corrosion control (Lead/Copper Rule) | TT= Treatment Technique (violation)
ETT= Enforcement Targeting Tool | PE= Public Education (requirement under Lead/Copper Rule) | TTHM= Total Trihalomethanes (Stage 1 Rule)
FANLs= Facility Analyte Level (refers to SW/DBP monitoring requirements) | PER= Preliminary Engineering Report | VOC= Volatile Organic Chemicals
GAC= Granular Activated Carbon | PN= Public Notice | VSW= Village Safe Water
GWUDI= Groundwater under the direct influence of surface water | PWS= Public Water System | WTP= Water Treatment Plant